## Slide 1: Variable Frequency Drives (VFD) in Industrial Refrigeration System
Cold Storage & Ice Plants
Submitted by: Mutyala Murali Manohar Krishna
Reg. No: RA2512053010009

## Slide 2
Controls AC motor speed via frequency & voltage
AC → DC (rectifier) → variable AC (inverter)
IGBT switching at 2–16 kHz using PWM
V/f or Vector (FOC) control modes
Eliminates fixed-speed energy waste
What is a VFD?
Compressor speed control (60–70% of power)
Condenser fan control – cube law savings
Evaporator fans – airflow matches demand
Brine / chilled water pump modulation
Lead-lag compressor pack configuration
Refrigeration Applications
Ice Plant Specific Uses
Screw/piston compressor matches ice load
Brine pump flow modulation at –10 to –18°C
Harvesting drive smooth acceleration
Cooling tower fans via wet-bulb feedback
Agitator/stirrer drives in brine-tank plants
Energy Savings – Affinity Laws
Flow ∝ Speed | Power ∝ Speed³
80% speed = only 51% power consumed
Compressors: 20–40% energy savings
Fans & Pumps: 50–70% savings
Payback period: typically, 6–18 months
Installation & Protection
Mount in 10–40°C clean electrical rooms
Shielded motor cables, 360° grounding
Line reactors (3–5%) for harmonic control
dV/dt output filters protect motor insulation
Built-in: overcurrent, thermal, phase-loss trips
Challenges & Future Trends
Harmonics: 12-pulse / AFE / active filters
Bearing currents → shaft grounding brushes
Min. compressor speed: 25–30 Hz enforced
SiC/GaN chips → >99% drive efficiency
IoT & solar PV thermal load shifting

## Slide 3
Thank You